## Slide 1: Bonitron, Inc.
Dedicated to engineering quality industrial electronics since 1962!
20130806

## Slide 2: Introduction
Est. 1962
Drive enhancements compatible
with all major drive manufacturers
Maximize process uptime
Designed and manufactured
in the U.S.A.

## Slide 3: Overview
Capacitor parameters
Capacitor aging
Solutions

## Slide 4: Electrolytic Capacitor
An electrolytic capacitor is a type of capacitor that uses an electrolyte to achieve a larger capacitance than other capacitor types. An electrolyte is a liquid or gel containing a high concentration of ions. Almost all electrolytic capacitors are polarized, which means that the voltage on the positive terminal must always be greater than the voltage on the negative terminal.
The benefit of large capacitance in electrolytic capacitors comes with several drawbacks as well. Among these drawbacks are large leakage currents, value tolerances, equivalent series resistance and a limited lifetime.

## Slide 5: Capacitor Parameters
Capacitors have capacitance
  How much energy can be stored per volt
Capacitors have equivalent series resistance
  ESR
  How much energy is lost trying to move energy in and out of the cap
  Causes cap to warm up during use
VFDs contain electrolytic capacitors

## Slide 6: Capacitor Aging
Electrolytic capacitors contain liquid electrolyte
  Tends to evaporate more when warm
Aging decreases capacitance
  <80% nameplate @ EOL
Aging increases ESR
  >200% nameplate @ EOL

## Slide 7: Capacitor / VFD Storage
Many installations have spare drives on the shelf for years
  Must be kept in temperature-controlled space
Electrolytic cap chemistry changes if not used
  Suddenly apply full voltage, and BANG!
Caps must be reformed before voltage is applied
  Raise voltage slowly over time
  M3628PCF, M3628ACF

## Slide 8: VFD Aging
Eventually, the VFD caps will fail
  Process will stop unexpectedly
Could preemptively replace…
  …but why, if you don’t have to?
Measure drive capacitance to determine aging
  M3628ACF Portable Capacitor Tester / Former

## Slide 9: Capacitor Reforming Guidelines
< 1 year and stored at rated temperature and humidity conditions (No reforming required)
1 – 2 years: Apply rated voltage, per the normal method, for 60 minutes under no load.
2 – 3 years: Using a DC power supply connected directly to the DC terminals of the product, ramp-up voltage from 0-100% of DC bus voltage (see table below) in steps of 25%. Dwell at 25%, 50% and 75% steps for 30 minutes each. At 100% voltage, dwell for 60 minutes, all under no load.
> 3 years: Using a DC power supply connected directly to the DC terminals of the product, ramp-up voltage from 0-100% of DC bus voltage (see table below) in steps of 25%. Dwell at each step for 120 minutes.
The forming voltage shall be 1.35 – 1.45 times the rated AC system voltage

## Slide 10: Capacitor Reforming Guidelines
Method 1 : When the capacitor is stocked for less than two years.
Switch the power on the converter for the time indicated in Fig.1.
Method 2A : When a DC power supply is used for reforming the capacitor, the current needs to be limited 500 mA.
Wait for 5 mins till the capacitor discharges.
Regulated DC power with active current limiting:
• Output current: 0.5…1 A DC, max. 500 mA during reforming
• Output voltage: adjustable 0…1000 V DC. An appropriate voltage during reforming is
1.35…1.45·Ux. Ux denotes the nominal AC voltage of the converter.
Fig. 1. Capacitor forming time vs non-operational time in years

## Slide 11: Reforming Curve

## Slide 12: Ultracapacitor Aging
Same aging problems apply to ultracaps
  Not in drives, typically used for energy storage banks
Ultracaps don’t need reforming
M3628PUT Portable Ultracapacitor Tester

## Slide 13: Standard VFD Voltages

## Slide 14: M3628 Comparison
 | PCF | ACF | PUT
Measures Capacitance | NO | YES | YES
Measures ESR | NO | NO | YES
Automatic Forming Profile | NO | YES | YES
Max Voltage | 900 VDC | 1000VDC | 130 VDC
Max Output Current | 1 ADC | 1ADC | 7 ADC
Max Load | 100,000 uF | 0.3 F | 500 kJ
Min Cycle Voltage |  |  | 5 VDC

## Slide 15: Summary
Capacitors and Ultracapacitors age and degrade.
M3628PCF can reform disused capacitors.
M3628ACT can reform and also measure capacitance 1000VDC -- good for 690Vac Drives.
M3628PUT Ultra-Caps only can measure capacitance and ESR.
  Can also reform, but not necessary.

## Slide 16: Maintenance Solutions
Battery Testers
Rapidly tests M3528B Battery Modules
Capacitor Dischargers
Depletes energy stored in ultracapacitors
Capacitor Formers
Form capacitors
Benchtop power supply
Capacitor Testers
Measure capacitance and ESR to determine when
end of life is reached
https://www.youtube.com/watch?v=lzH7dbczeZ4&t=5s
https://www.youtube.com/watch?v=543rPcwyqis&t=11s
PCF Operation Video
ACF Operation Video

## Slide 17: For More Information…
615-244-2825
Visit The Web site www.Bonitron.com
info@bonitron.com
Questions?
Training Videos
Manuals
Brochures
Unit Specifications
Contact Info
https://bonitron.com/PDFs/Manuals/Product_Overview_update_web_05_07_2024_new1.pdf
Complete Product Overview

## Slide 18
Dedicated to Designing and Manufacturing
Quality Industrial Electronics
BONITRON
WWW.BONITRON.COM
-
615-244-2825